## Slide 1
Eric Johnson
Dominion Energy South Carolina
Luke Booth and Joe Perigo
Schweitzer Engineering Laboratories, Inc.
A Case Study of a Shunt and Preexisting Series Simultaneous Fault
© 2025 Dominion Energy and SEL

## Slide 2: Outline
Introduce system, fault, and misoperation
Review root-cause analysis of misoperation
Discuss an open-phase detection method
Explain first-principles approach that aids in determining simultaneous faults

## Slide 3: Key takeaways
Learn clues that may indicate certain simultaneous faults
Understand an open-phase detection method
Realize phase-domain analysis is optional modern tool

## Slide 4: System one-line diagram

## Slide 5: System one-line diagram unknown series fault

## Slide 6: System one-line diagram simultaneous fault

## Slide 7: One-line diagram initial analysis
87
87
21

## Slide 8: Breaker 1 oscillography
Observations
C-phase current drastically increased
A-phase current is flat
A-phase and C-phase voltage decrease
Note: System is ACB phase rotation

## Slide 9: Breaker 2 oscillography
Observations
A-phase current increases more than C-phase current
A-phase and C-phase voltages move toward each other
A-phase voltage is greater than C-phase voltage

## Slide 10: Breaker 3 oscillography
Observations
A-phase current is significantly higher than C-phase current
A-phase voltage is greater than C-phase voltage

## Slide 11: Breaker 4 oscillography
Observations
A-phase current is significantly higher than C-phase current
Because A-phase current is higher than C-phase, zero-sequence current is present

## Slide 12: Breaker 3 primary relay residual current
Relays’ Responses
Primary relay momentarily enabled ground distance elements
Primary relay quadrilateral ground Zone 1 element operated on A-phase
Backup relay did not enable ground distance elements and did not operate

## Slide 13: Clues during fault to investigate
A-phase current of Breaker 1 is flat
  Can the CT secondary leads be shorted?
  It is unlikely that two sets of CTs are compromised
  What was the state of the current pre-fault?

## Slide 14: Pre-fault current Breaker 1 on Line 1
Observation
A-phase current is nonsinusoidal and close to zero

## Slide 15: Pre-fault current Breaker 2 on Line 1
Observation
A-phase current is sinusoidal and has primary current flowing

## Slide 16: Clues during fault to investigate
A-phase current of Breaker 1 is flat
  Can the CT secondary leads be shorted?
  It is unlikely that two sets of CTs are compromised
  What was the state of the current pre-fault?
  Asked field personnel to verify state of CTs

## Slide 17: Clues during fault to investigate
A-phase voltage is not depressing more than C-phase
  Is this a phase-to-phase fault or phase-to-phase-ground fault?
  Sequence network connections
Phase-to-phase fault
Phase-to-phase-ground fault

## Slide 18: Bus sequence voltages

## Slide 19: Pre-fault voltages and current on Line 1

## Slide 20: Known simultaneous fault condition

## Slide 21: Metered current on Line 1
Vector sum of Breaker 1 and 2 currents

## Slide 22: Open-phase detection – negative-sequence to positive-sequence ratio comparison
to

## Slide 23: Primary relay I2/I1 pre-fault comparison result

## Slide 24: Circuit analysis for simultaneous faults
Brief discussion of symmetrical components
Return to first principles – phase components
Circuit modeling
Simulation results

## Slide 25: Symmetrical components
Development in early-to-mid-1900s
Advancement for faulted circuit analysis
Applicable to simultaneous faults, but…

## Slide 26: Phase components
Kirchhoff’s voltage law (KVL) developed in mid-1800s
Requires modeling mutual coupling
Linear algebra can be pain point
But, in 2025, we have modern computing tools!

## Slide 27: Developing the circuit model

## Slide 28: Developing the circuit model

## Slide 29: Developing the circuit model

## Slide 30: Developing the circuit model

## Slide 31: Developing the circuit model

## Slide 32: Developing the circuit model

## Slide 33: Developing the circuit model

## Slide 34: Developing the circuit model
Known
Known
Unknown

## Slide 35: Developing the circuit model
Unknown
Known
Known

## Slide 36: Simulation results for C-A phase fault

## Slide 37: Simulation results for A-phase series fault

## Slide 38: Simultaneous fault

## Slide 39: Key takeaways
Learn clues that may indicate certain simultaneous faults
Understand an open-phase detection method
Realize phase-domain analysis is optional modern tool

## Slide 40: Questions?