## Slide 1
Mike Ramlachan, Craig Wester - GE Vernova
Case Study - Consolidating Monitoring with Protection

## Slide 2
Introduction
Dive into History – Establishing Requirements for Disturbance Monitoring
  PRC-002 and it’s many revisions
Monitoring Requirements
  SOE/SER
  TRF/FR
  DDR
Managing Monitoring Requirements
  Centralized
  De-Centralized
  Distributed
Monitoring Evolution
  PRC-028
Using a Relay to Meet Requirements
  Possible?
  Stimulate discussion

## Slide 3
August 14th, 2003 – North East Backout
Affecting parts of
  NJ/NY/CT/PA/MA/VT/OH/MI/Ontario/Quebec
Approximately 50 million people
Took up to 4 days to fully restore power
NERC task force established to investigate
  “NERC investigators labored over thousands of data items to synchronize the sequence of events, much like putting together small pieces of a very large puzzle. That process would have been significantly improved and sped up if there had been enough synchronized data recording devices”

## Slide 4
Monitoring Requirements Established
PRC-002-1 (2006)
  Disturbance Monitoring Equipment (DME) Requirements
PRC-018-1 (2006)
  Mandate DME installation and reporting of data per regional requirements
PRC-002-2 (2014)
  Consolidation of PRC-018-1 and PRC-002-1
Requirement for BES operators
  Enforceable by FERC
  Not a Standard but a requirement
Ensure adequate data is available for analysis of bulk electric system disturbances

## Slide 5
Disturbance Monitoring Requirements
Sequence of Events (SOE)
Fault Recording (FR) or Transient Fault Recording (TFR)
Dynamic Disturbance Recording (DDR)
Time synchronization accuracy
Sampling rate for FR and DDR
Data retention
Multifunctional Digital Fault Recorder
Time Synchronization
Communications
CT/VT Acquisition
Transducer Acquisition
Binary I/O
Traveling
Wave
Recorder
Waveform
Recorder
Disturbance
Recorder
Sequence- of-events (SOE)
Power
Quality
PMU
Continuous
Fault
Recorder

## Slide 6
Managing Requirements with Centralized Architecture
I, V
Protective Relay Triggers
Device Statuses
Other Signals
Advantages
Data captures simultaneously
Common platform
Suitable for small/medium S/S
Disadvantages
Directly wired requirement
Extensive copper wiring
Complicated for large S/S
Requires considerable design, construction and commissioning to implement and maintain
DFR

## Slide 7
Managing Requirements with De-Centralized Architecture
I, V, Protective Relay Triggers, Device Statuses, Other Signals
I, V, Protective Relay Triggers, Device Statuses, Other Signals
I, V, Protective Relay Triggers, Device Statuses, Other Signals
I, V, Protective Relay Triggers, Device Statuses, Other Signals
DFR
DAU
DAU
DAU
DAU
Advantages
Installed close to signal source
Simplified installation
Suitable for large S/S
Disadvantages
Communication can be proprietary
Synchronization required across data acquisition units (DAU)
Ideal for large transmission substations and capability for future expansion

## Slide 8
De-Centralized Architecture in Digital Substation
Advantages
IEC 61850 Standard
Non-proprietary
Ideal for Digital Substations
Simple
Disadvantages
Brownfield
IEC Process Interface Units (PIU) stream sample values (SV) to DME/Relays etc

## Slide 9
IEC 61850 DME Modeling
Multifunctional Digital Fault Recorder – IEC61850 Model
LD Base
LLN0
LTMS
LTIM
LCCH
LGOS
LSVS
LPHD
LD TW Rec
TW_RFLO
TW_RDRE
LD WF Rec
IMP_RFLO
WF_RDRE
LD Dist Rec
DIS_RDRE
DIS_MMXU
DIS_MSQI
DIS_MHAI
LD SOE Rec
SOE_RDRE
LD PQ
PQ_RDRE
PQ_MMXU
PQ_MSQI
PQ_MHAI
LD PMU
PMU_MMXU
PMU_MMXN
PMU_MSQI
PMU_GGIO
LD POW
POW_TCTR
POW_TVTR
POW_TGSN
POW_GGIO
LD Analog Acquisition
RABR
SV_TVTR
SV_TCTR
LD Transducers
RABR
LD Binary I/O
RBDR
GOOSEIN_GGIO
PIU
TW TCTR/TVTR
TCTR/TVTR
TGSN
GGIO/XSWI/XCBR

## Slide 10
Managing Requirements with Distributed Architecture
I, V, Protective Relay Triggers, Device Statuses, Other Signals
I, V, Device Statuses, Other Signals
I, V, Device Statuses, Other Signals
I, V, Device Statuses, Other Signals
Ethernet Switch
Data Concentrator
PDC
DFR
PAC
Relay
PAC
Relay
PAC
Relay
Advantages
Installed close to signal source
Simplified installation
Cost effective
Disadvantages
Phasor Measurement Unit (PMU) or similar requirement for DDR
Synchronization needed and required across all devices
Complicated architecture
Option for Brownfield installations to minimize operational impact and cost

## Slide 11
Monitoring Evolution
NERC Project 2021-04 created to evaluate and modify PRC-002 in 2 Phases
Phase 1 – notification of data and identify BES owners needing the data
  Establish clarity around stations with multiple owners BES equipment
  R1 and R5 enhanced
  R13 added – offering flexibility to meet requirements
  PRC-002-4 adopted in early 2023
Phase 2 – address gaps as identified by the inverter-based resource (IBR) performance task force (IRPTF)
  IRPTF concerned criteria not adequate for IBR resources and many will fall out of scope
  IBR requirements removed from PRC-002
  New PRC-028-1 established to address IBRs
  PRC-002-5 and PRC-028-1 adopted in October 2023
PRC-002 requirements might not be adequate as the power system evolves

## Slide 12
Can Modern Relays meet Requirements
PRC-002-5 and PRC-028-1 may potentially increase need for additional DMEs
SOE – Possibly Capable
FR – Not Capable
  Triggered record length of 3 minutes
  C37.232 (COMNAME)
  PRC-028-1 requirement of 128 samples per cycle
DDR – Not Capable
  Recording of up to 10 days
Data Retention an issue – lack of adequate storage

## Slide 13
Conclusions
Current generation of relays cannot meet all requirements
Storage (data retention) deficiency
  Storage cost have drastically come down in the last decade
  Should not be a technical or economic roadblock for next generation relays
Sampling rate deficiency
  Some relays on the market today are capable of sampling rates of 128 s/c
Virtualization/Containerization helps
  Separation of real time and non-real time processes

## Slide 14
Thank You
Questions?