## Slide 1
Sathish Kumar Mutha, Arun Shrestha, and Sajal Harmukh
Schweitzer Engineering Laboratories, Inc.
Improved Multi-Ended Impedance-Based Fault Locating for Untransposed Transmission Lines
© 2025 SEL

## Slide 2: Outline
Traditional approach
  Background
  Untransposed-error analysis
Proposed approach
  Sequence coupling line-parameters (Z21 and Z20) estimation
  Fault-location estimation
Simulation and field-events results
Limitations

## Slide 3: Traditional approach

## Slide 4: Traditional approach
Sequence domain network equation under fault condition

## Slide 5: Traditional approach
Sequence domain network equation under fault condition
Assume a fully transposed line

## Slide 6: Traditional approach
Sequence domain network equation under fault condition
Assume a fully transposed line
0
0

## Slide 7: Traditional approach
Sequence domain network equation under fault condition

## Slide 8: Traditional approach
Sequence domain network equation under fault condition

## Slide 9: Traditional approach – unbalanced faults
Negative-sequence network equation

## Slide 10: Traditional approach – unbalanced faults
Negative-sequence network equation
Transposed approximation approach (= =0)

## Slide 11: Traditional approach – unbalanced faults
Negative-sequence network equation
Transposed approximation approach (= =0)
m

## Slide 12: Traditional approach – unbalanced faults
Negative-sequence network equation
Transposed approximation approach (= =0)
m
Errors in Traditional Approach

## Slide 13: Untransposed-error analysis
Error terms in traditional approach

## Slide 14: Untransposed-error analysis
Error terms in traditional approach
Using superposition principle

## Slide 15: Untransposed-error analysis
Error terms in traditional approach
Using superposition principle

## Slide 16: Untransposed-error analysis
Error terms in traditional approach
Using superposition principle

## Slide 17: Untransposed-error analysis
Error terms in traditional approach
Using superposition principle

## Slide 18: Untransposed-error analysis
Error terms in traditional approach
Using superposition principle

## Slide 19: Untransposed-error analysis
Load-current-based errors
Positive-sequence load-current-based error
Zero-sequence load-current-based error
Fault-current-based errors
Positive-sequence fault-current-based error
Zero-sequence fault-current-based error

## Slide 20: Traditional approach – simulation results
FL estimates – 400 kV system horizontal tower configuration
Source-impedance ratios,
  SIRS = 1
  SIRR = 1
Fault location = 50 km
Line length = 100 km
TP = Transposed line UTP = Untransposed line

## Slide 21: Traditional approach – simulation results
FL estimates – 400 kV system horizontal tower configuration
Source-impedance ratios,
  SIRS = 1
  SIRR = 1
Fault location = 50 km
Line length = 100 km
Load-current-based errors
TP = Transposed line UTP = Untransposed line

## Slide 22: Traditional approach – simulation results
FL estimates – 400 kV system - horizontal tower configuration
Load angle fixed at 1 degree
Line length = 100 km
Pure-fault current-based errors

## Slide 23: Traditional approach – simulation results
FL estimates – 400 kV system - horizontal tower configuration
Load angle fixed at 1 degree
Line length = 100 km
Pure-fault current-based errors

## Slide 24: Traditional approach – simulation results
FL estimates – 400 kV system - horizontal tower configuration
Load angle fixed at 1 degree
Line length = 100 km
Pure-fault current-based errors

## Slide 25: Traditional approach – simulation results
FL estimates – 400 kV system - horizontal tower configuration
Load angle fixed at 1 degree
Line length = 100 km
Pure-fault current-based errors

## Slide 26: Traditional approach – simulation results
FL estimates – 400 kV system - horizontal tower configuration
Load angle fixed at 1 degree
Line length = 100 km
Pure-fault current-based errors

## Slide 27: Parameters neglected in traditional approach
Summary – errors

## Slide 28: Parameters neglected in traditional approach
Summary – errors
Z21 – sequence impedance coupling from positive-sequence network to negative-sequence network

## Slide 29: Parameters neglected in traditional approach
Summary – errors
Z21 – sequence impedance coupling from positive-sequence network to negative-sequence network
Z20 – sequence impedance coupling from zero-sequence network to negative-sequence network

## Slide 30: Proposed approach – unbalanced faults

## Slide 31: Proposed approach – unbalanced faults
Estimates Z21 and Z20 using pre-fault data

## Slide 32: Proposed approach – unbalanced faults
Estimates Z21 and Z20 using pre-fault data
Includes Z21 and Z20 in faulted negative-sequence network

## Slide 33: Proposed approach – unbalanced faults
Estimates Z21 and Z20 using pre-fault data
Includes Z21 and Z20 in faulted negative-sequence network
Solves network for fault location

## Slide 34: Z21 estimation
Applying KVL to above circuit
Pre-fault negative-sequence network

## Slide 35: Z20 estimation
(Single-circuit Tx line sequence impedance matrix)
Interesting symmetry in sequence domain

## Slide 36: Z01 estimation
Pre-fault zero-sequence network

## Slide 37: Z01 estimation
Applying KVL to above circuit
+
Pre-fault zero-sequence network

## Slide 38: Z01 estimation
Applying KVL to above circuit
+
Pre-fault zero-sequence network

## Slide 39: Z01 estimation
Applying KVL to above circuit
+
Pre-fault zero-sequence network

## Slide 40: Y11 estimation
Pre-fault positive-sequence network

## Slide 41: Y11 estimation
(x = S, R)
Pre-fault positive-sequence network

## Slide 42: Y11 estimation
(x = S, R)
Apply KCL to above circuit
Pre-fault positive-sequence network

## Slide 43: I1 compensation
Current flowing in Tx line
Pre-fault positive-sequence network

## Slide 44: Y21 estimation and I2 compensation
Pre-fault negative-sequence network

## Slide 45: Y21 estimation and I2 compensation
Apply KCL to above circuit
Pre-fault negative-sequence network

## Slide 46: Y21 estimation and I2 compensation
Apply KCL to above circuit
Current flowing in Tx line
Pre-fault negative-sequence network

## Slide 47: Y01 estimation and I0 compensation
Apply KCL to above circuit
Current flowing in Tx line
Pre-fault zero-sequence network

## Slide 48: Summary – steps for Z21 and Z20 estimation
Estimate admittance line parameters (Y11, Y21, and Y01)
Compensate sequence currents (I1, I2, and I0)
Estimate Z21 using negative-sequence network Estimate Z20 using zero-sequence network
Estimate admittance distribution factors (k1S and k1R)

## Slide 49: Proposed approach – unbalanced faults
Faulted negative-sequence network

## Slide 50: Proposed approach – unbalanced faults
Faulted negative-sequence network

## Slide 51: Phasor simulation results
Systems tested
400 kV system – single-circuit transmission line with horizontal tower configuration
400 kV system – single-circuit transmission line with vertical tower configuration
230 kV system – single-circuit transmission line with right-triangle tower configuration
230 kV system – double-circuit transmission line
400 kV system – double-circuit transmission line
System conditions
SIRS = 0.1 – SIRR varied from 1 to 5 in steps of 0.5
SIRS = 1 – SIRR varied from 1 to 5 in steps of 0.5

## Slide 52: Phasor simulation results
SIRS = 0.1
SIRR = 1
Z21 Mag error < 1.2%
Z21 Ang error < 1 deg
Z21 estimates – 400 kV system, horizontal tower configuration

## Slide 53: Phasor simulation results
SIRS = 0.1
SIRR = 1
Z20 Mag error < 5.5 %
Z20 Ang error < 0.5 deg
Z20 estimates – 400 kV system, horizontal tower configuration

## Slide 54: Phasor simulation results
SIRS = 1
SIRR = 1
Fault location = 50 km
Line length= 100 km
Load-current-based errors
FL estimates – 400 kV system, horizontal tower configuration

## Slide 55: Phasor simulation results
Load angle = 1 degree
Line length = 100 km
Pure-fault-current-based errors
FL estimates – 400 kV system, horizontal tower configuration

## Slide 56: Phasor simulation results
Simulation test variables
SIRS = 0.1
Fault locations (km) -> 30, 50, 80
Load angle (deg) -> –20, –10, –5, 5, 10, 20
Fault type -> AG, BG, CG, AB, BC, CA, ABG, BCG, CAG
Fault resistance -> 0.001, 10, 40
Worst-case FL error – 400 kV system, horizontal tower configuration

## Slide 57: Phasor simulation results
Worst-case FL error for various tower configurations
Chart: Absolute Error (km)
| 400 kV Horizontal tower configuration | 400 kV Vertical tower configuration | 230 kV Right angle tower configuration | 230 kV double-circuit tower configuration | 400 kV double-circuit tower configuration
Traditional Approach—Worst-case Error (km) | 10.58 | 12.12 | 7.35 | 11.15 | 13.01
Proposed Approach—Worst-case Error (km) | 0.33 | 0.42 | 0.38 | 4 | 5.72

## Slide 58: Field event results
Absolute FL error for five field events
Chart: Field Event
Traditional Approach - Error (km) | 1.08 | 1.61 | 0.39 | 0.62 | 0.58
Proposed Approach - Error (km) | 0.67 | 0.24 | 0.19 | 0.02 | 0.13

## Slide 59: Proposed approach
Limitations
Line-parameter (Z1L, Z0L) errors
CT, PT errors
Double-circuit lines
Intermittently-transposed transmission lines

## Slide 60: Conclusion
Proposed approach
Estimates sequence-mutual-coupling parameters in negative-sequence network accurately
Requires no extra inputs from user
Accurately estimates fault location while eliminating untransposed errors
Results from simulations and real-world events demonstrate the effectiveness and robustness of our method

## Slide 61
Questions?