## Slide 1
Cleofas Rojas Los Angeles Department of Water and Power
Aadityaa Padmanabhan Electric Power Research Institute
Mohit Sharma and Amanvir Sudan Schweitzer Engineering Laboratories, Inc.
Mutual Coupling in Subtransmission Systems—A Real-World Experience
© 2025 Los Angeles Department of Water and Power, Electric Power Research Institute, and SEL

## Slide 2: Outline
Mutual coupling phenomenon
System description
System modeling and simulation results
Utility’s subtransmission protection philosophy
Misoperation event analysis
Lessons learned

## Slide 3: Electromagnetic coupling
Electromagnetic coupling is not just a transmission phenomenon
At ac peak, magnetic field intensity is the highest
Shorter distance between conductors yields higher magnetic coupling

## Slide 4: Self- and mutual impedance matrix

## Slide 5: Two parallel circuits
Circuit X
Circuit Y
Circuit X
Circuit Y

## Slide 6: Two parallel circuits
Voltage drop on Circuit X due to current flow on Circuit Y
Voltage drop on Circuit Y due to current flow on Circuit X
Circuit X
Circuit Y
Circuit X
Circuit Y

## Slide 7: Two parallel circuits
Sequence translation
Circuit X
Circuit Y

## Slide 8: Net magnetic flux

## Slide 9: System description
FDR 4 and FDR 5 are 5 miles long
No ground wires
477 26/7 ACSR conductors
9 ft average spacing between FDR 4 and FDR 5

## Slide 10: Modeling and simulation results
Fault simulated on FDR 5 and I0 induced on mutually coupled FDR 4
Length of mutual coupling segment varied from 0–5 miles in steps of 0.5 miles
Observations
Higher induced I0 for longer mutually coupled length
Higher induced I0 when remote-end breaker of FDR 5 is open
Maximum induced I0 ~50% of ground fault level on that feeder
Chart: Mutually Coupled Line Distance
| 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5
No Outage | 0 | 20 | 41 | 61 | 82 | 103 | 124 | 145 | 167 | 189 | 212
Remote-End Open | 0 | 40 | 80 | 121 | 161 | 201 | 242 | 283 | 324 | 366 | 408

## Slide 11: Modeling and simulation results
Fault simulated on FDR 5 and I0 induced on mutually coupled FDR 4
Length of mutual coupling segment varied from 0–5 miles in steps of 0.5 miles
Observations
Higher induced I0 for longer mutually coupled length
Higher induced I0 when remote-end breaker of FDR 5 is open
Maximum induced I0 ~50% of ground fault level on that feeder
Chart: Mutually Coupled Line Distance
| 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5
No Outage | 0 | 0.02 | 0.04 | 0.06 | 0.08 | 0.1 | 0.12 | 0.14 | 0.16 | 0.18 | 0.21
Remote-End Open | 0 | 0.02 | 0.04 | 0.07 | 0.09 | 0.11 | 0.14 | 0.16 | 0.18 | 0.2 | 0.23

## Slide 12: System description
25-mile lines
5-mile feeders
No ground wires
1,351.5 54/19 ACSR conductors
25 ft spacing between Line 3 and FDR 1

## Slide 13: Modeling and simulation results
Chart: Mutually Coupled Line Distance
| 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5
No Outage | 0 | 37 | 75 | 115 | 157 | 202 | 252 | 309 | 374 | 451 | 545
Remote-End Open | 0 | 88 | 177 | 268 | 360 | 456 | 556 | 661 | 773 | 893 | 1023
Chart: Mutually Coupled Line Distance
| 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5
No Outage | 0 | 0.04 | 0.07 | 0.11 | 0.15 | 0.2 | 0.24 | 0.3 | 0.36 | 0.44 | 0.53
Remote-End Open | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.26 | 0.31 | 0.37 | 0.43 | 0.5 | 0.57

## Slide 14: Subtransmission protection philosophy at utility
Lines originate from 34.5 kV RS bus and terminate at DS
RS end: Nondirectional 51
  51 pickup: 2x emergency line rating
  Coordination interval: 15–18 cycles
DS end: Directional 51
  51 pickup: 1.25x emergency line rating
  Coordination interval: 15–18 cycles

## Slide 15: Event analysis
AG fault occurred on FDR 5
R3, R4, R2, and R1 picked up on 51N
51N in R2 was supervised by 32QF
R4 tripped open first on 51AT

## Slide 16: Event analysis
R3
R2

## Slide 17: Event analysis
AG fault on FDR 5

## Slide 18: Event analysis
R2

## Slide 19: Event analysis
R3 tripped 5–6 cycles after R4 opened its breaker
R3 initiated autoreclose
Autoreclose in all 4 relays was set to 1 shot to lock out with 10-second open interval timer

## Slide 20: Event analysis
R3 sent close command and Breaker 3 was successfully closed
R2 tripped on 51NT, which never reset during entire reclosing cycle of R3
R1 did not trip

## Slide 21: Event analysis
R3
R2

## Slide 22: Event analysis
R2 finally tripped

## Slide 23: Mitigation strategies
Can we change ground directional priority and preference?
ORDER = Q
ORDER = QV

## Slide 24: Mitigation strategies
Can we change positive-sequence current restraint factor A2?
A2 engages directional enable
A2 must be chosen to provide dependability for its own feeder fault
A2 = 0.5 is the highest value to have dependability for all fault types

## Slide 25: Directional element characteristic for R2

## Slide 26: Mitigation strategies
Can we increase ground overcurrent pickups?
51N pickup should be selected based on worst-case mutual coupling but should maintain sensitivity for coordination
Mutual coupling effects due to operational switching should be considered
Worst-case mutual coupling also depends on system configuration – common bus on both ends, common bus only on one end, isolated buses on both ends

## Slide 27: Mitigation strategies
Can we change fault detector pickups – 50QFP and 50QRP?
50QFP and 50QRP are also inputs to directional enable logic
Raising 50QFP might work but must confirm dependability for all unbalanced faults on its own feeder/line
I2.Mag in our case study = 66 A primary = 1.2375 A secondary

## Slide 28: Conclusion
Effects of mutual coupling should be modeled even for subtransmission networks
Modeling should be considered when 10% line is coupled
32Q is a superior directional element on mutually coupled lines due to voltage drop caused by Z0M but it is also prone to misoperations
With some tweaks in directional enable logic of 32Q, security can be established

## Slide 29
Questions?