## Slide 1
NERC Update
Protection Standards and Data Center Fault
JP Skeath, Manager, Engineering and Security Integration
Annual Georgia Tech Fault and Disturbance Conference
May 5, 2025

## Slide 2: Order 901 Summary

## Slide 3: Milestone 2 Summary
Installation of disturbance monitoring equipment
Share data on request
New PRC-029
Performance based ride-through criteria
Capability based ride-through criteria
New PRC-030
Analysis of performance during a disturbance
Initiates what is evaluated for ride-through performance
New PRC-028

## Slide 4: Milestone 2 Summary
Installation of disturbance monitoring equipment
Share data on request
New PRC-029
Performance based ride-through criteria
Capability based ride-through criteria
New PRC-030
Analysis of performance during a disturbance
Triggers what is evaluated for ride-through performance
New PRC-028
77.8%
70.88%
83.85%
Out for NOPR

## Slide 5: Milestone 2 Summary – Other Affected Standards
Project 2021-04 – Modifications to PRC-002-5
  Final Ballot of 84.2%
  Excluded IBRs, minor clarifications on CSV headers
Project 2020-02 – Modifications to PRC-024-4
  Final Ballot of 86.41%
  Focused on synchronous generation. Added applicability for synchronous condensers

## Slide 6: Load Loss Incident

## Slide 7: Load Loss Incident – Affected Load
Load Lost During Event
(GREEN)

## Slide 8: Load Loss Incident – Affected Load

## Slide 9: Load Loss Incident – Affected Load
Exclusively Data Center load
25-30 substations
~ 60 individual data center load points
Individual load loss ranged from 2 MW to 85 MW

## Slide 10: Load Loss Effects - Frequency
Frequency rises to 60.047

## Slide 11: Load Loss Effects - Voltage
High Voltage
Less than 1.1 per unit
Operators removed local area 230 kV capacitor banks to reduce voltage

## Slide 12: Event Analysis

## Slide 13: Event Analysis
The load did not come back immediately

## Slide 14: Event Analysis
Something Else Happened
????

## Slide 15: Data Center Coalition Input
Cooling load is critical after voltage disturbance
Design follows ITIC curve
Will “lockout” after a number of events in a specific period of time
More than one power distribution architecture
Data Center Load

## Slide 16: Data Center Coalition Input
Cooling load is critical after voltage disturbance
Design follows ITIC curve
Will “lockout” after a number of events in a specific period of time
More than one power distribution architecture
Data Center Load

## Slide 17: The rest of the story…

## Slide 18: Event Analysis Results
3 Strikes…
You’re Out!

## Slide 19: Incident Review Considerations
Require dynamic response models of large loads in facility interconnection requirements
Perform studies to determine the potential magnitude of load loss for system disturbances (particularly faults)
Take into consideration the potential for voltage-sensitive load loss when configuring automatic reclosing schemes

## Slide 20: Next steps/Needs
We need to understand this ride through response looks like for all facilities

## Slide 21: NERC Large Loads Task Force
Identify and characterize unique aspects and risks of Large Loads
Large Load definition
Identify gaps and potential risk mitigation
Develop guidance and best practice

## Slide 22: Forced Oscillations

## Slide 23
Questions and Answers
John Paul “JP” Skeath
Manager, Engineering and Security Integration
North American Electric Reliability Corporation
3353 Peachtree Road NE, Suite 600 – North Tower
Atlanta, GA 30326
404-446-9630 office | 404-823-1365 cell
Email: John.Skeath@nerc.net