## Slide 1
By Gary Kobet and Ulyana Elliott
TVA Response to GMD event
05/10/2024 through 05/13/2024

## Slide 2: Contents
TVA Monitoring Network
Summary
TVA GIC Measurements
Weakley GIC Blocker
TVA Magnetometer Data
Harmonics
Source: https://www.reseau-teria.com/en/high-solar-activity-what-impact-will-it-have-on-your-gnss-device/

## Slide 3: TVA Monitoring Network
GIC Detector | Magnetometer
Anderson | Ackerman
Bradley | Allen
Bull Run | Bull Run
East Point | Colbert
Gleason | Gallatin
Johnsonville | John Sevier
Madison 1 | Lagoon Creek
Madison 2 | Paradise
Montgomery 2 | Raccoon Mountain
Paradise 5 | Shawnee
Paradise 6 | Union
Paradise 7 | Watts Bar
Pin Hook | 
Raccoon Mountain | 
Rutherford | 
Shelby | 
Southaven | 
Sullivan 3 | 
Union 1 | 
Weakley | 
Widows Creek 10 | 
Widows Creek 17 | 

## Slide 4: Summary
TVA began noticing effects 5/10/2024 at about 10:00AM system time (15:00UTC)
Highest GICs at Montgomery (44Adc) and Union (41Adc)
  These sites continue to seem to nearly mirror each other
  Data available from Anderson, Bull Run, Bradley, East Point, Gleason, Montgomery 2, Johnsonville, Paradise 7, Pin Hook 2, Raccoon Mountain, Shelby, Southaven, Sullivan 3, Union 1, Weakley, Widows Creek 17
  No data available from Madison 1 or 2, Limestone, Paradise 5 or 6, Widows Creek 10
Weakley GIC blocker inserted 12 times from 5/10/2024@12:05 system time to 5/12/2024@23:39 system time
  Longest insertion time was a little over 2 hours (5/10/2024 from 13:58:21 to 16:00:39 system time)
Slight increase in system harmonics
  No cap bank trips due to harmonics

## Slide 5: TVA GIC Measurements Two highest sites: Montgomery & Union
Times are UTC (EST is UTC-5hrs)
Union
Montgomery
178 mi (286km)

## Slide 6: TVA GIC Measurements Montgomery: Peak GIC -44Adc
Union
Montgomery
178 mi (286km)
Peak GIC -44Adc on 5/11/2024@0207UTC
(5/10/2024@2107 system time-EST)
Times are UTC (EST is UTC-5hrs)

## Slide 7: TVA GIC Measurements Union: Peak GIC -40Adc
Union
Montgomery
178 mi (286km)
Peak GIC -40Adc on 5/10/2024@2235UTC
(5/10/2024@1735 system time-EST)
Times are UTC (EST is UTC-5hrs)

## Slide 8: TVA GIC Measurements Montgomery & Union Banks MVAR
Peak MVAR on 5/11/2024@about 1430 system time (1930UTC) (no correlation to peak GIC)

## Slide 9: TVA GIC Measurements Montgomery & Union Banks MVAR losses
Bank MVAR losses (no correlation to peak GIC)

## Slide 10: TVA GIC Measurements Montgomery Banks MVAR losses

## Slide 11: TVA GIC Measurements Union Banks MVAR losses

## Slide 12: Weakley GIC blocker
NBD = Neutral Blocking Device

## Slide 13: Weakley GIC blocker Resistor-Capacitor Ratings

## Slide 14: Weakley GIC blocker GIC Blocker – normal state
CT1
CT2
CT3
VP1
Transformer neutral solidly grounded

## Slide 15: Weakley GIC blocker GIC Blocker – inserted
When GIC in excess of 5Adc:
DC Breaker opens
DC Breaker aux contact opens AC Breaker
DC Breaker re-closes
AC Breaker remains open
CT1
CT2
CT3
VP1

## Slide 16: Weakley GIC blocker GIC Blocker – return to normal
Once the power system event has cleared:
If no GIC present (VP1<5V for 1hr), remains solidly grounded (closed breaker assembly)
CT1
CT2
CT3
VP1

## Slide 17: Weakley GIC blocker Weakley GIC Measurements
1
Weakley GIC blocker had 12 insertions during the GMD storm
2
3
4
5
6
7
8
9
10
11
12

## Slide 18: Weakley GIC blocker Johnsonville & Gleason GIC
Weakley
GIC Detector
Neutral Blocker
Johnsonville
Gleason
Times are UTC (EST is UTC-5hrs)
Change in Johnsonville/Gleason GIC when Weakley GIC blocker inserts 12:05:54EST

## Slide 19: TVA Magnetometer Data-North
*
*https://www.mathworks.com/help/map/choose-a-3-d-coordinate-system.html

## Slide 20: TVA Magnetometer Data-East
*
*https://www.mathworks.com/help/map/choose-a-3-d-coordinate-system.html

## Slide 21: TVA Magnetometer Data-Down
*
*https://www.mathworks.com/help/map/choose-a-3-d-coordinate-system.html

## Slide 22: TVA Harmonic Measurements
slight increase, considered insignificant

## Slide 23
Aurora borealis visible from Signal Mountain, TN around 11:30PM EDT on Friday, May 10th, 2024.
Questions?