## Slide 1
Dr. Ryan Said, Dr. Martin Murphy, Brooke Pearson, Hans Loewenheath
Vaisala Xweather
Understanding and interpreting lightning data
Agenda:
Lightning Locating System (LLS) applications
How an LLS works
Interpreting and using LLS data

## Slide 2: Applications of LLS data

## Slide 3: A cloud-to-ground flash consists of one or more return strokes
Rakov and Uman, 2003, Ch4
Return strokes last for tens of microseconds
Peak current
Max rate-of-rise
Notes: Any kind of lightning that hits a turbine transfers electrical current, which can cause damage
The distribution of these current parameters vary by type of lightning
Let’s take a look at a negative CG flash
This diagram from a textbook shows three views
Panel a shows what a long-exposure photo might look like, with a branched structure of the downward negative leader
Panel b shows time on the x-axis, imagine rotating the camera during the flashes. Panel c shows the current at the channel base on the same time axis
What you see is a current surge when the stepped leader makes contact with the upward connecting leader. This leads to a return stroke that lasts for a few tens of microseconds.
There’s then a calm period, and we might see one or more subsequent return strokes with their own current surges
The peak current in these events can range from a few kA to several hundred kA
There may also be something called a continuing current, which is much lower in amplitude, around a few hundred amps, but it can last for 1000 times as long – 10s or 100s of milliseconds
Positive CG strokes typically have just one return stroke are more likely to have a continuing current

## Slide 4: Precision lightning data provides real-time correlation of lightning-caused faults
Lightning strikes to infrastructure can cause flashovers and faults
  Flashover: voltage spike from a lightning strike to a phase or shielding wire, causing a line-to-ground fault
  Backflashover: line-to-ground fault initiated by insufficiently grounded tower
  Induced voltage spikes from lightning a strike nearby
Fault current causes breakers to trip and a momentary outage
Lightning Data Verification:
  Time & Location Correlation – Match stroke timestamp and error-ellipse location with transient recorder data to confirm a lightning‐caused trip
  Peak Current Estimate – Stroke amplitude (kA) indicates strike severity and the likelihood of flashover

## Slide 5: Historical lightning records reveal the exposure along a line
10-year NLDN Cloud-to-ground (CG) strike-point density
2015-2024 (inclusive)

## Slide 6: How a Lightning Location System (LLS) Works

## Slide 7: Lightning Locating Systems (LLS) use remote sensors and a central analyzer to determine latitude, longitude, time, and more
Remote sensors:
  Detect radio-frequency signals generated by lightning
  Stream to central analyzer: Time of Arrival (TOA), Magnetic Direction Finding (MDF), amplitude, and other parameters
Central analyzer:
  Finds sensor reports produced by the same lightning source
  Calculates latitude, longitude, time + other characteristics of each lightning event using observations from multiple sensors

## Slide 8: Vaisala combines angle of arrival (MDF) and TOA location methods
Location with 5 sensors using a combination of MDF and TOA
MDF TOA Combined DF+TOA
Optimize solution by minimizing squared errors between all observed and calculated times/angles
Provides a network with more uniform coverage and more resilience to sensor outages

## Slide 9
Photo © 1984 by Johnny Autery
IC pulse
CG first stroke
CG subsequent stroke
Lightning signal shapes are used to determine if lightning hit the ground
Photo © 1994 by Ron Holle
Notes: Features of the shapes (“waveforms”) are used in classification: telling the difference between what hits ground and what stays in the cloud

## Slide 10
Peak current and sensor amplitude are linearly correlated at a fixed distance
Step 1: Range-normalize sensor amplitudes to 100 km:
Step 2: Convert RNSS to channel-base peak current. Assuming lowest portion of lightning channel acts as a transmission line, normalized amplitude is linearly related to peak current
Idone, V.P. et al. 1993: J. Geophys. Res., 98, 18323-18332

## Slide 11: LLS Performance

## Slide 12: Performance is determined by how much and how well lightning is detected
Location Accuracy (LA): how close to the real location did we get?
Detection Efficiency (DE): what fraction (or percentage) of the lightning is detected?
Classification Accuracy: how well did we differentiate between CG strokes and IC pulses?
Notes:   LA relevant to individual return strokes in CG flashes
  expressed by median, due to skewed & one-sided distribution

## Slide 13: The LLS estimates the location accuracy for each event by calculating an error ellipse at the 50th percentile confidence level
Confidence region (50th percentile)
Probability density follows 2D joint Gaussian distribution
Ellipse determined by:
  Time and angle uncertainty at each sensor
  Sensor locations
  Solution location
Semi-major axis
Semi-minor axis
Notes: Lightning position is at center of ellipse
Probability level determines the probability that the actual lightning event is somewhere inside the ellipse
Semi-major axis provides a single number that represents the worst-case location error

## Slide 14: A typical CG flash in the NLDN has 50% error ellipses with better than 200-meter axes
1 km
CG strokes (7)
IC pulse (1)
Notes: Small ellipse axes will be allowed later in 2025 to provide the accuracy closer to reality, instead of over-inflated when well located.

## Slide 15: Ellipses are scalable with the probability level depending on desired confidence
kilometers E-W
kilometers N-S
50%
90%
99%
Probability levels
The 50th percentile ellipse is reported with each stroke
If desired probability level is given as a fraction p (0-1) then:

## Slide 16: Lightning correlating to a fault is very rarely calculated to be far away, e.g. 5 mi
Real customer case:
4 kA: very low current
Detected by only 2 sensors
Fairly uncommon on both points...
Reported error ellipse allows for poorly-located events to be correlated
Notes: Time correlation gives one clue
Ellise collision with a line gives another clue

## Slide 17: Detection Efficiency model incorporates sensor response, propagation effects, and source amplitudes
Sensor response: sensor detection threshold and saturation
Propagation effects: geometric spreading and exponential decay
Source amplitudes: Integrate across distribution of expected effective peak currents (eg CG or IC)
For each location:
Identify detection probability at each sensor based on the arrival amplitude
Consider all combinations of sensors that may contribute
Calculate distribution of error ellipses and accumulated detection probability
Typical CG flash DE > 95%

## Slide 18: Effects of bidirectional classification errors are impacted by the distribution
Positive polarity events
Negative polarity events
IC pulses
IC pulses
A few misclassified +IC events results in a flood of misclassified +CG
Some misclassification of negative events also occurs, but the net effect is less severe
Overall rate of misclassification for all events of both polarities is around 5-10%
Chart: 
| IC pulses | CG strokes
Correctly classified | 0.85 | 0.05
Misclassified | 0 | 0.1
Chart: 
| IC pulses | CG strokes
Correctly classified | 0.4 | 0.5
Misclassified | 0.05 | 0.05

## Slide 19: If fault correlation query shows zero CGs, try including IC events in the query
Case from August 2021
With IC events included
Power line fault in this general area
Lightning was observed but all classified as “IC,” when actually one may have been a CG
Query of CG only
Notes: Make sure to point out that most are actually IC, but likely just one was actually a CG

## Slide 20: Major data fields include time, latitude, longitude, type, and signal strength (kA)

## Slide 21: Summary
Real-Time Fault Monitoring: Cloud-to-ground stroke reports correlate with fault records to confirm lightning-induced faults
Confidence & Classification: Understanding the network’s error-ellipse metrics, peak current accuracy, detection efficiency, and classification accuracy ensure you can reliably attribute outages to lightning (and rule out other causes)
Long-Term Diagnostics: Aggregated lightning archives reveal recurring hot spots and failure modes