## Slide 1
Julian Oelhaf1, Georg Kordowich2, Andreas Maier1, Johann Jäger2, and Siming Bayer1 1Pattern Recognition Lab 2Institute of Electrical Energy Systems Friedrich-Alexander-University Erlangen-Nuremberg, Germany
Unsupervised Clustering for Fault Analysis in Power Systems

## Slide 2: Germany’s Energiewende - Chance and Challenges
Notes: Renewable Energy Growth caused Increased Complexity in Power Systems - More renewable sources like wind and solar add variability, making grid management more complex.
Massive Data from Decentralized Grids Distributed generation and smart technologies generate vast amounts of data, overwhelming traditional analysis methods.
Fault and Disturbance Analysis Challenge: Difficulty in Identifying and Responding to Issues With more components and data, detecting and responding to faults in real-time becomes increasingly challenging.

## Slide 3: Challenges In Modern Power System Protection
Bartz/Stockmar, CC BY-SA 4.0, https://creativecommons.org/licenses/by-sa/4.0, via Wikimedia Commons.
Notes: Bi-directional Power Flow: Increased complexity due to reverse power flow and distributed generation sources (e.g., renewables).
More Components in the Grid: Growing number of components such as distributed energy resources (DERs), storage, and smart devices.
More Sensors/Measurements: Expanding sensor networks for real-time monitoring, leading to high-volume, high-dimensional data.
More Data: Massive influx of data from sensors, SCADA systems, and digital twins, creating challenges in storage, processing, and analysis.
ML as a Potential Solution: Machine learning (ML) methods offer scalable, adaptive solutions for protection, fault detection, and predictive maintenance.
Lack of Labels/Ground Truths: Inadequate labeled data for supervised learning, making it difficult to train models and validate predictions.

## Slide 4: Motivation
Power system disturbances and faults produce complex data that’s hard to analyze manually.
Fast, reliable event understanding is critical for protection, control, and system reliability.
Unsupervised clustering enables automatic grouping of events for better analysis and decision support.
Notes: Power system faults and disturbances produce complex, high-frequency waveform data
Engineers need to extract insights from large volumes of unlabeled disturbance records
Manual analysis is time-consuming and not scalable
Fast, reliable event understanding is critical for protection, control, and system reliability
Unsupervised clustering enables automatic grouping of similar events for better analysis and decision support

## Slide 5: Problem statement
How can we automatically discover and interpret meaningful patterns in large-scale, unlabeled power system disturbance data using unsupervised clustering methods?

## Slide 6: Dataset Overview: RTE Electrical Signals Database
Operator: RTE – France’s national transmission system operator
  Grid Scale: 60,000+ miles of high-voltage lines, 2,800+ substations, 50Hz
Release: Publicly available since May 2024
Content: Real-world measurements from France’s high-voltage transmission network
Focus: Captures electrical signals during events such as faults and switching operations
Notes: https://upload.wikimedia.org/wikipedia/commons/thumb/1/1f/RTE_logo.svg/2048px-RTE_logo.svg.png

## Slide 7: What we know (about the Dataset)
12,053 disturbance events recorded on 90 kV lines
Each recording has 6 signals (v1, v2, v3, i1, i2, i3) with 21,000 data points
  ~3.28s

## Slide 8: What we don't know (about the Dataset)
The fault types or classifications—no labels are provided.
The fault locations or conditions under which faults occurred.

## Slide 9: Alternative title: What to do, if your neighbor doesn’t talk to you.
Notes: https://upload.wikimedia.org/wikipedia/commons/thumb/c/c3/Flag_of_France.svg/2560px-Flag_of_France.svg.png
https://upload.wikimedia.org/wikipedia/commons/2/21/Flag_of_Germany_%283-2%29.svg
https://upload.wikimedia.org/wikipedia/commons/thumb/d/db/France_Germany_Locator_%28Europe%29.svg/1200px-France_Germany_Locator_%28Europe%29.svg.png

## Slide 10: Which disturbance can be observed here?

## Slide 11: What type of fault can be observed here?

## Slide 12: Dataset
Each sample contains 6 channels: three voltage, three current
Nr. of datapoints per sample:

## Slide 13: Task
We need a framework for the systematic analysis of an unlabeled dataset to gain insight into the disturbances.

## Slide 14: Dataset
Each sample contains 6 channels: three voltage, three current
Nr. of datapoints per sample:
Need to reduce the datapoints per sample

## Slide 15: Feature Extraction
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 16: Feature Extraction
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 17: Feature Extraction
Feature
Space
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
(Number of datapoints per sample)
VOLTAGE
CURRENT
Notes: Shape of FFT: (10500, 6)

## Slide 18: Feature Reduction
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 19: Feature Reduction
Simplify Data: Reduce feature complexity for efficiency.
Prevent Overfitting: Focus on relevant features.
Enhance Interpretability: Make fault patterns easier to analyze.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 20: Feature Reduction
Simplify Data: Reduce feature complexity for efficiency.
Prevent Overfitting: Focus on relevant features.
Enhance Interpretability: Make fault patterns easier to analyze.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Principal Component Analysis (PCA)

## Slide 21: Problem: Linear Transformation
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Notes: Explain the graph here. Each dot is a sample. X and Y is the entire signal reduced to two features/dimensions.

## Slide 22: Problem: Linear Transformation
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Solution: Non-Linear Transformation

## Slide 23: Dimensionality Reduction: PCA or t-SNE?
PCA: Linear, fast, reduces dimensions while preserving variance.
t-SNE: Non-linear, captures complex patterns but computationally expensive.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 24: Dimensionality Reduction: PCA or t-SNE?
PCA: Linear, fast, reduces dimensions while preserving variance.
t-SNE: Non-linear, captures complex patterns but computationally expensive.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
How to be fast and non-linear?

## Slide 25: Dimensionality Reduction: PCA + t-SNE
PCA: Linear, fast, reduces dimensions while preserving variance.
t-SNE: Non-linear, captures complex patterns but computationally expensive.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Solution: PCA → t-SNE: Reduce dimensions with PCA, then use t-SNE for detailed visualization.

## Slide 26: Dimensionality Reduction: PCA + t-SNE

## Slide 27: Feature Clustering
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 28: -Means Clustering
Input: Raw data, divided into K groups based on similarity.
Output: Data points grouped into clusters, refined through iterations.
Pros & Cons: Efficient and scalable but requires a set number of groups and struggles with outliers and irregular data patterns.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Lloyd, Stuart. "Least squares quantization in PCM." IEEE transactions on information theory 28.2 (1982): 129-137.
MacQueen, James. "Some methods for classification and analysis of multivariate observations." Proceedings of the Fifth Berkeley Symposium on Mathematical Statistics and Probability, Volume 1: Statistics. Vol. 5. University of California press, 1967.

## Slide 29: Initial Data Analysis
Dataset includes a wide range of disturbances:
  different short-circuits, transients, switching events, downstream load connections, high-impedance faults, busbar switching, and other anomalies
In total, 10+ distinct disturbance types observed
Optimal balance found at K = 15, capturing meaningful structure without overfitting
Notes: Exploring Different Values for K (Number of Clusters)
High K:
  Results in overly granular clusters, leading to fragmentation and complexity.
  Can cause overfitting and difficulty in interpretation.
Low K:
  Produces broad, mixed clusters with reduced interpretability.
  May underfit the model, missing finer patterns.
K as a Heuristic:
  Selecting K is a balancing act, guided by methods like the elbow method.
  The choice depends on the specific context and desired model complexity.

## Slide 30: Cluster Analysis
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 31: Key Assumptions
The dataset contains multiple types of faults and disturbance events
15 clusters provide a reasonable trade-off between detail and interpretability, based on exploratory analysis
Events with similar electrical characteristics (features) are expected to group into the same cluster

## Slide 32
K-Means clustering based on t-SNE features

## Slide 33: Comparison of Cluster Distribution
PCA
t-SNE

## Slide 34: 🧪 Hypothesis
If unsupervised clustering effectively captures the structure of the data, then manually labeled samples within each cluster should exhibit high consistency — enabling meaningful interpretation of entire clusters.

## Slide 35: Analysis of Manually Labeled Clustering Results
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 36: Cluster Interpretation via Manual Labeling
Labeled a representative subset of 205 samples to evaluate clustering results
Assessed label consistency within clusters to validate cluster coherence
Event Type Label
Normal
Short-circuit
Switching
Transients
Other
Unknown
Notes: We conducted a detailed manual labeling of each sample, including attributes such as Sample ID, Event Type, Fault Class, Fault Type, and Affected Phase(s). However, for the sake of brevity and clarity in this presentation, we will focus solely on the Event Type when discussing cluster interpretation.

## Slide 37: Event Distribution per Cluster
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Normal | 0 | 0.5 | 0 | 0 | 0.17647 | 0.22222 | 0.21429 | 0.85714 | 0 | 0.4 | 0 | 0 | 0 | 0.61538 | 0
Other | 0 | 0.125 | 0 | 0 | 0.058824 | 0 | 0 | 0.071429 | 0 | 0.3 | 0.058824 | 0 | 0 | 0.076923 | 0
Short-circuit | 0.090909 | 0.1875 | 0.076923 | 0.66667 | 0.52941 | 0.44444 | 0.5 | 0 | 1 | 0.1 | 0.82353 | 0.88235 | 0.77778 | 0.23077 | 0.91667
Switching | 0.86364 | 0 | 0.84615 | 0.22222 | 0.23529 | 0.11111 | 0.21429 | 0 | 0 | 0 | 0 | 0.058824 | 0 | 0 | 0.083333
Transients | 0 | 0.1875 | 0 | 0.11111 | 0 | 0.22222 | 0 | 0.071429 | 0 | 0.2 | 0 | 0 | 0 | 0.076923 | 0
Unknown | 0.045455 | 0 | 0.076923 | 0 | 0 | 0 | 0.071429 | 0 | 0 | 0 | 0.11765 | 0.058824 | 0.22222 | 0 | 0
Clusters

## Slide 38: Cluster With Primarily Normal Events
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Normal | 0 | 0.5 | 0 | 0 | 0.17647 | 0.22222 | 0.21429 | 0.85714 | 0 | 0.4 | 0 | 0 | 0 | 0.61538 | 0
Other | 0 | 0.125 | 0 | 0 | 0.058824 | 0 | 0 | 0.071429 | 0 | 0.3 | 0.058824 | 0 | 0 | 0.076923 | 0
Short-circuit | 0.090909 | 0.1875 | 0.076923 | 0.66667 | 0.52941 | 0.44444 | 0.5 | 0 | 1 | 0.1 | 0.82353 | 0.88235 | 0.77778 | 0.23077 | 0.91667
Switching | 0.86364 | 0 | 0.84615 | 0.22222 | 0.23529 | 0.11111 | 0.21429 | 0 | 0 | 0 | 0 | 0.058824 | 0 | 0 | 0.083333
Transients | 0 | 0.1875 | 0 | 0.11111 | 0 | 0.22222 | 0 | 0.071429 | 0 | 0.2 | 0 | 0 | 0 | 0.076923 | 0
Unknown | 0.045455 | 0 | 0.076923 | 0 | 0 | 0 | 0.071429 | 0 | 0 | 0 | 0.11765 | 0.058824 | 0.22222 | 0 | 0
Notes: Cluster 7: 12 Normal

## Slide 39
K-Means Clustering Based on t-SNE Features

## Slide 40: Clusters With Primarily Switching Events
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Normal | 0 | 0.5 | 0 | 0 | 0.17647 | 0.22222 | 0.21429 | 0.85714 | 0 | 0.4 | 0 | 0 | 0 | 0.61538 | 0
Other | 0 | 0.125 | 0 | 0 | 0.058824 | 0 | 0 | 0.071429 | 0 | 0.3 | 0.058824 | 0 | 0 | 0.076923 | 0
Short-circuit | 0.090909 | 0.1875 | 0.076923 | 0.66667 | 0.52941 | 0.44444 | 0.5 | 0 | 1 | 0.1 | 0.82353 | 0.88235 | 0.77778 | 0.23077 | 0.91667
Switching | 0.86364 | 0 | 0.84615 | 0.22222 | 0.23529 | 0.11111 | 0.21429 | 0 | 0 | 0 | 0 | 0.058824 | 0 | 0 | 0.083333
Transients | 0 | 0.1875 | 0 | 0.11111 | 0 | 0.22222 | 0 | 0.071429 | 0 | 0.2 | 0 | 0 | 0 | 0.076923 | 0
Unknown | 0.045455 | 0 | 0.076923 | 0 | 0 | 0 | 0.071429 | 0 | 0 | 0 | 0.11765 | 0.058824 | 0.22222 | 0 | 0
Notes: Cluster 0: 19 events Switching
Cluster 2: 11 events Switching

## Slide 41
K-Means Clustering Based on t-SNE Features

## Slide 42: Clusters With Primarily Short-Circuits Events
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Normal | 0 | 0.5 | 0 | 0 | 0.17647 | 0.22222 | 0.21429 | 0.85714 | 0 | 0.4 | 0 | 0 | 0 | 0.61538 | 0
Other | 0 | 0.125 | 0 | 0 | 0.058824 | 0 | 0 | 0.071429 | 0 | 0.3 | 0.058824 | 0 | 0 | 0.076923 | 0
Short-circuit | 0.090909 | 0.1875 | 0.076923 | 0.66667 | 0.52941 | 0.44444 | 0.5 | 0 | 1 | 0.1 | 0.82353 | 0.88235 | 0.77778 | 0.23077 | 0.91667
Switching | 0.86364 | 0 | 0.84615 | 0.22222 | 0.23529 | 0.11111 | 0.21429 | 0 | 0 | 0 | 0 | 0.058824 | 0 | 0 | 0.083333
Transients | 0 | 0.1875 | 0 | 0.11111 | 0 | 0.22222 | 0 | 0.071429 | 0 | 0.2 | 0 | 0 | 0 | 0.076923 | 0
Unknown | 0.045455 | 0 | 0.076923 | 0 | 0 | 0 | 0.071429 | 0 | 0 | 0 | 0.11765 | 0.058824 | 0.22222 | 0 | 0
Notes: Cluster 8: 12 events Short-Circuits
Cluster 10: 14 events Short-Circuits
Cluster 11: 15 events Short-Circuits
Cluster 12: 7 events Short-Circuits
Cluster 14: 11 events Short-Circuits

## Slide 43
K-Means Clustering Based on t-SNE Features

## Slide 44: Discussion
Unsupervised clustering reveals structure in large, unlabeled fault datasets but lacks prior knowledge for validation.
Feature transformation impacts clustering quality—t-SNE improves fault separation compared to PCA alone.
Cluster interpretability remains challenging, with external factors (e.g., sensor variations) potentially influencing results.

## Slide 45: Conclusion
K-Means clustering helps structure large datasets, aiding initial fault analysis and reducing expert workload.
Limitations include low silhouette scores and manual validation constraints, highlighting the need for alternative methods.
Future work should explore hybrid models, alternative clustering techniques, and simulated data for validation.

## Slide 46: Thank you! Questions?
Funding
This project was funded by the Deutsche Forschungsgemeinschaft (DFG, German Research Foundation) - 535389056.
Contact
Julian Oelhaf Pattern Recognition Lab Department of Computer Science Friedrich-Alexander University Erlangen-Nürnberg Erlangen, GERMANY
julian.oelhaf@fau.de
Notes: https://www.dfg.de/resource/blob/196772/815c8be8174a278bbac1de13d2b43210/logo-international-267-data.png

## Slide 47: Germany's Energiewende
Notes: The Problem

## Slide 48: Overview
Artificial Intelligence
Pattern Recognition
Machine Learning
Notes: Machine Learning as a potential solution

## Slide 49: Feature Extraction
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Fast Fourier Transform (FFT) transforms time-series data into frequency-domain features
Normalization standardizes spectral magnitudes
  Enhancing model generalization and comparison.
Assumption: Frequency patterns are indicative of fault types, such as short circuits, open-circuits, and unbalanced faults.

## Slide 50: Feature Extraction

## Slide 51: Feature Extraction

## Slide 52: Feature Extraction

## Slide 53: One Problem: Curse of Dimensionality
Original Data: 21,000 samples × 6 channels = 126,000 features
After FFT: 10,500 frequency components × 6 channels = 63,000 features
Challenge: Too many features for effective comparison and analysis
Solution: Feature Reduction Techniques to simplify and improve model performance
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 54: PCA
Dimensionality Reduction: Projects data into a lower-dimensional space while preserving variance.
Linear Transformation: Finds principal components that maximize variance in the data.
Fast and Scalable: Efficiently handles large datasets with a clear mathematical foundation.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Are there any drawbacks?
Wold, Svante, Kim Esbensen, and Paul Geladi. "Principal component analysis." Chemometrics and intelligent laboratory systems 2.1-3 (1987): 37-52.

## Slide 55: Principal Component Analysis (PCA)
Image Source: https://www.ibm.com/content/dam/connectedassets-adobe-cms/worldwide-content/creative-assets/s-migr/ul/g/89/56/2-1_orthogonal-relshp_pc1-pc2-1.png

## Slide 56: t-Distributed Stochastic Neighbor Embedding
Non-linear Dimensionality Reduction: Maps high-dimensional data to a lower dimension while preserving local structures.
Visualizes Clusters: Reveals complex relationships and clusters in the data.
Computationally Intensive: Effective for smaller datasets due to high computational cost.
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis
Van der Maaten, Laurens, and Geoffrey Hinton. "Visualizing data using t-SNE." Journal of machine learning research 9.11 (2008).

## Slide 57
Created with: https://www.naftaliharris.com/blog/visualizing-k-means-clustering/

## Slide 58: Dimensionality Reduction: PCA
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 59: Dimensionality Reduction: t-SNE
Feature Extraction
Feature Reduction
Feature Clustering
Cluster Analysis

## Slide 60
Plots for manual labeling

## Slide 61: Cluster Distribution for PCA Features

## Slide 62: Visual Cluster Analysis
PCA
t-SNE

## Slide 63
K-Means clustering based on PCA features

## Slide 64: Cluster Distribution for t-SNE Features

## Slide 65: Cluster Metrics
Method/Metric | Purity ↑ | Entropy ↓ | NMI ↑ | ARI ↑ | Silhouette ↑
K-Means PCA | 0.608 | 0.767 | 0.305 | 0.113 | -0.744
K-Means t-SNE | 0.720 | 1.095 | 0.328 | 0.115 | -0.399

## Slide 66: Example of Voltage Signal

## Slide 67: Example of Current Signal

## Slide 68: Example of combined signals